## Change Logs
Meridian Networks NDS Workbook
| Document Number: |  | Revision: 1.0 | Effective Date: 5/15/2026
Meridian Networks - Phoenix DC Build Phase 1 Integration Details Document
Revision History
Revision | Effective Date | Changes Made |  | Content Owner/Modifer | Approved By
1 | 2026-05-16 | Initial Document |  | James Rodriguez - Meridian Networks
1.2 | 2026-05-26 | Removed Agg to Agg and Edge to Edge connections, and updated the BOM to reflect the changes on the cables qty. |  | James Rodriguez - Meridian Networks
1.2a | 2026-06-03 | Correct some typos, on the network layout to reflect all 10 meters and the correct modules m1 and 4 and ports from the mgmt switch and console to the new additional Sup modules. |  | James Rodriguez - Meridian Networks
1.3 | 2026-06-16 | Added the new Transceivers requested, and updated the BOM and power layout to reflect the new 400V 32A PDUs |  | James Rodriguez - Meridian Networks
1.3a | 2026-06-26 | changed the Tabs name to reflect rack names 501 to 504 |  | James Rodriguez - Meridian Networks

## Rack Elevation
Front View
| Rack: R0501-SP-A (Spine Switch A) |  |  |  |  | Rack: R0502-SP-B (Spine Switch B) |  |  |  |  | Rack: R0503-LF-A (Leaf Switch A) |  |  |  |  | Rack: R0504-LF-B (Leaf Switch B)
| RU | Chassis Rack Layout - Front |  |  |  | RU | Chassis Rack Layout - Front |  |  |  | RU | Chassis Rack Layout - Front |  |  |  | RU | Chassis Rack Layout - Front
| 48 | LC/LC Patch Panel #SP-A-PP1 (AzureNet) |  |  |  | 48 | LC/LC Patch Panel #SP-A-PP2 (AzureNet) |  |  |  | 48 | LC/LC Patch Panel Unidentified |  |  |  | 48 | LC/LC Patch Panel Unidentified
| 47 |  |  |  |  | 47 |  |  |  |  | 47 | Blank panel |  |  |  | 47 | Blank panel | P1 going to Media Converter in rack 0501
| 46 | Blank panel |  |  |  | 46 | Blank panel |  |  |  | 46 | Blank panel |  |  |  | 46 | Blank panel
| 45 | Blank panel |  |  |  | 45 | Blank panel |  |  |  | 45 | Blank panel |  |  |  | 45 | Blank panel
| 44 | Horizontal Cable Manager |  |  |  | 44 | Blank panel |  |  |  | 44 | Blank panel |  |  |  | 44 | Blank panel
| 43 | Blank panel |  |  |  | 43 | Blank panel |  |  |  | 43 | Blank panel |  |  |  | 43 | Blank panel
| 42 | Blank panel |  |  |  | 42 | Blank panel |  |  |  | 42 | Blank panel |  |  |  | 42 | Blank panel
| 41 | Horizontal Cable Manager |  |  |  | 41 | Blank panel |  |  |  | 41 | Blank panel |  |  |  | 41 | Blank panel
| 40 | OOB Management Switch |  |  |  | 40 | Blank panel |  |  |  | 40 | Blank panel |  |  |  | 40 | Blank panel
| 39 | FS.COM Media Converter | Lashing bar (front) |  |  | 39 | Blank panel |  |  |  | 39 | Blank panel |  |  |  | 39 | Blank panel
| 38 | Console Server (Open Gear Front) |  |  |  | 38 | Blank panel |  |  |  | 38 | Blank panel |  |  |  | 38 | Blank panel
| 37 |  |  |  |  | 37 | Blank panel |  |  |  | 37 | Blank panel |  |  |  | 37 | Blank panel
| 36 | Blank panel |  |  |  | 36 | Blank panel |  |  |  | 36 | Blank panel |  |  |  | 36 | Blank panel
| 35 | Blank panel |  |  |  | 35 | Blank panel |  |  |  | 35 | Blank panel |  |  |  | 35 | Blank panel
| 34 | Blank panel |  |  |  | 34 | Blank panel |  |  |  | 34 | Blank panel |  |  |  | 34 | Blank panel
| 33 | Blank panel |  |  |  | 33 | Blank panel |  |  |  | 33 | Blank panel |  |  |  | 33 | Blank panel
| 32 | Blank panel |  |  |  | 32 | Blank panel |  |  |  | 32 | Blank panel |  |  |  | 32 | Blank panel
| 31 | Blank panel |  |  |  | 31 | Blank panel |  |  |  | 31 | Blank panel |  |  |  | 31 | Blank panel
| 30 | Blank panel |  |  |  | 30 | Blank panel |  |  |  | 30 | Blank panel |  |  |  | 30 | Blank panel
| 29 | Blank panel |  |  |  | 29 | Blank panel |  |  |  | 29 | Blank panel |  |  |  | 29 | Blank panel
| 28 | Blank panel |  |  |  | 28 | Blank panel |  |  |  | 28 | Blank panel |  |  |  | 28 | Blank panel
| 27 | Blank panel |  |  |  | 27 | Blank panel |  |  |  | 27 | Blank panel |  |  |  | 27 | Blank panel
| 26 | Blank panel |  |  |  | 26 | Blank panel |  |  |  | 26 | Blank panel |  |  |  | 26 | Blank panel
| 25 | Blank panel |  |  |  | 25 | Blank panel |  |  |  | 25 | Blank panel |  |  |  | 25 | Blank panel
| 24 | Blank panel |  |  |  | 24 | Blank panel |  |  |  | 24 | Blank panel |  |  |  | 24 | Blank panel
| 23 | Blank panel |  |  |  | 23 | Blank panel |  |  |  | 23 | Blank panel |  |  |  | 23 | Blank panel
| 22 | 2U Cables Passthrough (for Network cables) |  |  |  | 22 | 2U Cables Passthrough (for Network cables) |  |  |  | 22 | 2U Cables Passthrough (for Network cables) |  |  |  | 22 | 2U Cables Passthrough (for Network cables)
| 21 |  |  |  |  | 21 |  |  |  |  | 21 |  |  |  |  | 21
| 20 | Spine Router A Cisco N9K-C9508 Chassis Ports Side |  |  |  | 20 | Spine Router B Cisco N9K-C9508 Chassis Ports Side |  |  |  | 20 | Leaf Switch A Cisco N9K-C9508 Chassis Ports Side |  |  |  | 20 | Leaf Switch B Cisco N9K-C9508 Chassis Ports Side
| 19 |  |  |  |  | 19 |  |  |  |  | 19 |  |  |  |  | 19
| 18 |  |  |  |  | 18 |  |  |  |  | 18 |  |  |  |  | 18
| 17 |  |  |  |  | 17 |  |  |  |  | 17 |  |  |  |  | 17
| 16 |  |  |  |  | 16 |  |  |  |  | 16 |  |  |  |  | 16
| 15 |  |  |  |  | 15 |  |  |  |  | 15 |  |  |  |  | 15
| 14 |  |  |  |  | 14 |  |  |  |  | 14 |  |  |  |  | 14
| 13 |  |  |  |  | 13 |  |  |  |  | 13 |  |  |  |  | 13
| 12 |  |  |  |  | 12 |  |  |  |  | 12 |  |  |  |  | 12
| 11 |  |  |  |  | 11 |  |  |  |  | 11 |  |  |  |  | 11
| 10 |  |  |  |  | 10 |  |  |  |  | 10 |  |  |  |  | 10
| 9 |  |  |  |  | 9 |  |  |  |  | 9 |  |  |  |  | 9
| 8 |  |  |  |  | 8 |  |  |  |  | 8 |  |  |  |  | 8
| 7 |  |  |  |  | 7 |  |  |  |  | 7 |  |  |  |  | 7
| 6 |  |  |  |  | 6 |  |  |  |  | 6 |  |  |  |  | 6
| 5 |  |  |  |  | 5 |  |  |  |  | 5 |  |  |  |  | 5
| 4 | 2U Cables Passthrough (for Power cords) |  |  |  | 4 | 2U Cables Passthrough (for Power cords) |  |  |  | 4 | 2U Cables Passthrough (for Power cords) |  |  |  | 4 | 2U Cables Passthrough (for Power cords)
| 3 |  |  |  |  | 3 |  |  |  |  | 3 |  |  |  |  | 3
| 2 | Blank panel |  |  |  | 2 | Blank panel |  |  |  | 2 | Blank panel |  |  |  | 2 | Blank panel
| 1 | Blank panel |  |  |  | 1 | Blank panel |  |  |  | 1 | Blank panel |  |  |  | 1 | Blank panel
Rear View
| Rack: R0206-CA-B (Aggregation B) |  |  |  |  | Rack: R0503-CA-A (Leaf Switch A) |  |  |  |  | Rack: R0502-CE-B (Cloud Edge A) |  |  |  |  | Rack: R0501-CE-A (Cloud Edge A)
PDU A | RU | Chassis Rack Layout - Rear |  | PDU B | PDU A | RU | Chassis Rack Layout - Rear |  | PDU B | PDU A | RU | Chassis Rack Layout - Rear |  | PDU B | PDU A | RU | Chassis Rack Layout - Rear |  | PDU B
| 48 | LC/LC Patch Panel Unidentified (Rear) | 48 |  |  | 48 | LC/LC Patch Panel Unidentified (Rear) | 48 |  |  | 48 | LC/LC Patch Panel #CE-A-PP2 (Azure) Rear | 48 |  |  | 48 | LC/LC Patch Panel #CE-A-PP1 (Azure) Rear | 48
| 47 |  | 47 |  |  | 47 |  | 47 |  |  | 47 |  | 47 |  |  | 47 |  | 47
| 46 |  | 46 |  |  | 46 |  | 46 |  |  | 46 |  | 46 |  |  | 46 |  | 46
| 45 |  | 45 |  |  | 45 |  | 45 |  |  | 45 |  | 45 |  |  | 45 |  | 45
| 44 |  | 44 |  |  | 44 |  | 44 |  |  | 44 |  | 44 |  |  | 44 |  | 44
| 43 |  | 43 |  |  | 43 |  | 43 |  |  | 43 |  | 43 |  |  | 43 |  | 43
| 42 |  | 42 |  |  | 42 |  | 42 |  |  | 42 |  | 42 |  |  | 42 |  | 42
| 41 |  | 41 |  |  | 41 |  | 41 |  |  | 41 |  | 41 |  |  | 41 |  | 41
| 40 |  | 40 |  |  | 40 |  | 40 |  |  | 40 |  | 40 |  |  | 40 | OOB Management Switch (rear) | 40
| 39 |  | 39 |  |  | 39 |  | 39 |  |  | 39 |  | 39 |  |  | 39 |  | 39
| 38 |  | 38 |  |  | 38 |  | 38 |  |  | 38 |  | 38 |  |  | 38 | Console Server (Open Gear Rear) | 38
| 37 |  | 37 |  |  | 37 |  | 37 |  |  | 37 |  | 37 |  |  | 37 |  | 37
| 36 |  | 36 |  |  | 36 |  | 36 |  |  | 36 |  | 36 |  |  | 36 |  | 36
| 35 |  | 35 |  |  | 35 |  | 35 |  |  | 35 |  | 35 |  |  | 35 |  | 35
| 34 |  | 34 |  |  | 34 |  | 34 |  |  | 34 |  | 34 |  |  | 34 |  | 34
| 33 |  | 33 |  |  | 33 |  | 33 |  |  | 33 |  | 33 |  |  | 33 |  | 33
| 32 |  | 32 |  |  | 32 |  | 32 |  |  | 32 |  | 32 |  |  | 32 |  | 32
| 31 |  | 31 |  |  | 31 |  | 31 |  |  | 31 |  | 31 |  |  | 31 |  | 31
| 30 |  | 30 |  |  | 30 |  | 30 |  |  | 30 |  | 30 |  |  | 30 |  | 30
| 29 |  | 29 |  |  | 29 |  | 29 |  |  | 29 |  | 29 |  |  | 29 |  | 29
| 28 |  | 28 |  |  | 28 |  | 28 |  |  | 28 |  | 28 |  |  | 28 |  | 28
| 27 |  | 27 |  |  | 27 |  | 27 |  |  | 27 |  | 27 |  |  | 27 |  | 27
| 26 |  | 26 |  |  | 26 |  | 26 |  |  | 26 |  | 26 |  |  | 26 |  | 26
| 25 |  | 25 |  |  | 25 |  | 25 |  |  | 25 |  | 25 |  |  | 25 |  | 25
| 24 |  | 24 |  |  | 24 |  | 24 |  |  | 24 |  | 24 |  |  | 24 |  | 24
| 23 |  | 23 |  |  | 23 |  | 23 |  |  | 23 |  | 23 |  |  | 23 |  | 23
| 22 |  | 22 |  |  | 22 |  | 22 |  |  | 22 |  | 22 |  |  | 22 |  | 22
| 21 |  | 21 |  |  | 21 |  | 21 |  |  | 21 |  | 21 |  |  | 21 |  | 21
| 20 | Spine Router B Cisco N9K-C9508 Chassis | 20 |  |  | 20 | Spine Router A Cisco N9K-C9508 Chassis | 20 |  |  | 20 | Spine Router B Cisco N9K-C9508 Chassis | 20 |  |  | 20 | Spine Router A Cisco N9K-C9508 Chassis | 20
| 19 |  | 19 |  |  | 19 |  | 19 |  |  | 19 |  | 19 |  |  | 19 |  | 19
| 18 |  | 18 |  |  | 18 |  | 18 |  |  | 18 |  | 18 |  |  | 18 |  | 18
| 17 |  | 17 |  |  | 17 |  | 17 |  |  | 17 |  | 17 |  |  | 17 |  | 17
| 16 |  | 16 |  |  | 16 |  | 16 |  |  | 16 |  | 16 |  |  | 16 |  | 16
| 15 |  | 15 |  |  | 15 |  | 15 |  |  | 15 |  | 15 |  |  | 15 |  | 15
| 14 |  | 14 |  |  | 14 |  | 14 |  |  | 14 |  | 14 |  |  | 14 |  | 14
| 13 |  | 13 |  |  | 13 |  | 13 |  |  | 13 |  | 13 |  |  | 13 |  | 13
| 12 |  | 12 |  |  | 12 |  | 12 |  |  | 12 |  | 12 |  |  | 12 |  | 12
| 11 |  | 11 |  |  | 11 |  | 11 |  |  | 11 |  | 11 |  |  | 11 |  | 11
| 10 |  | 10 |  |  | 10 |  | 10 |  |  | 10 |  | 10 |  |  | 10 |  | 10
| 9 |  | 9 |  |  | 9 |  | 9 |  |  | 9 |  | 9 |  |  | 9 |  | 9
| 8 |  | 8 |  |  | 8 |  | 8 |  |  | 8 |  | 8 |  |  | 8 |  | 8
| 7 |  | 7 |  |  | 7 |  | 7 |  |  | 7 |  | 7 |  |  | 7 |  | 7
| 6 |  | 6 |  |  | 6 |  | 6 |  |  | 6 |  | 6 |  |  | 6 |  | 6
| 5 |  | 5 |  |  | 5 |  | 5 |  |  | 5 |  | 5 |  |  | 5 |  | 5
| 4 |  | 4 |  |  | 4 |  | 4 |  |  | 4 |  | 4 |  |  | 4 |  | 4
| 3 |  | 3 |  |  | 3 |  | 3 |  |  | 3 |  | 3 |  |  | 3 |  | 3
| 2 |  | 2 |  |  | 2 |  | 2 |  |  | 2 |  | 2 |  |  | 2 |  | 2
| 1 |  | 1 |  |  | 1 |  | 1 |  |  | 1 |  | 1 |  |  | 1 |  | 1

## Rack-SP-A (501)
RU | Chassis Rack Layout - Front |  | PDU A | RU | Chassis Rack Layout - Rear |  | PDU B
48 | LC/LC Patch Panel #SP-A-PP1 (AzureNet) |  |  | 48 | LC/LC Patch Panel #SP-A-PP1 (AzureNet) Rear | 48
47 |  |  |  | 47 |  | 47
46 | Blank panel |  |  | 46 |  | 46
45 | Blank panel |  |  | 45 |  | 45
44 | Horizontal Cable Manager |  |  | 44 |  | 44
43 | Blank panel |  |  | 43 |  | 43
42 | Blank panel |  |  | 42 |  | 42
41 | Horizontal Cable Manager |  |  | 41 |  | 41
40 | OOB Management Switch |  |  | 40 | OOB Management Switch (rear) | 40
39 | TP-Link Media Converter | Lashing bar (front) |  | 39 |  | 39
38 | Console Server (Open Gear Front) |  |  | 38 | Console Server (Open Gear Rear) | 38
37 |  |  |  | 37 |  | 37
36 | Blank panel |  |  | 36 |  | 36
35 | Blank panel |  |  | 35 |  | 35
34 | Blank panel |  |  | 34 |  | 34
33 | Blank panel |  |  | 33 |  | 33
32 | Blank panel |  |  | 32 |  | 32
31 | Blank panel |  |  | 31 |  | 31
30 | Blank panel |  |  | 30 |  | 30
29 | Blank panel |  |  | 29 |  | 29
28 | Blank panel |  |  | 28 |  | 28
27 | Blank panel |  |  | 27 |  | 27
26 | Blank panel |  |  | 26 |  | 26
25 | Blank panel |  |  | 25 |  | 25
24 | Blank panel |  |  | 24 |  | 24
23 | Blank panel |  |  | 23 |  | 23
22 | 2U Cables Passthrough (for Network Cables) |  |  | 22 |  | 22
21 |  |  |  | 21 |  | 21
20 | Spine Router A Cisco N9K-C9508 Chassis Ports Side |  |  | 20 | Spine Router A Cisco N9K-C9508 Chassis | 20
19 |  |  |  | 19 |  | 19
18 |  |  |  | 18 |  | 18
17 |  |  |  | 17 |  | 17
16 |  |  |  | 16 |  | 16
15 |  |  |  | 15 |  | 15
14 |  |  |  | 14 |  | 14
13 |  |  |  | 13 |  | 13
12 |  |  |  | 12 |  | 12
11 |  |  |  | 11 |  | 11
10 |  |  |  | 10 |  | 10
9 |  |  |  | 9 |  | 9
8 |  |  |  | 8 |  | 8
7 |  |  |  | 7 |  | 7
6 |  |  |  | 6 |  | 6
5 |  |  |  | 5 |  | 5
4 | 2U Cables Passthrough (for Power cords) |  |  | 4 |  | 4
3 |  |  |  | 3 |  | 3
2 | Blank panel |  |  | 2 |  | 2
1 | Blank panel |  |  | 1 |  | 1
https://example.com

## Rack-SP-B (502)
RU | Chassis Rack Layout - Front | PDU A | RU | Chassis Rack Layout - Rear |  | PDU B
48 | LC/LC Patch Panel #SP-A-PP2 (AzureNet) |  | 48 | LC/LC Patch Panel #SP-A-PP2 (AzureNet) Rear | 48
47 |  |  | 47 |  | 47
46 | Blank panel |  | 46 |  | 46
45 | Blank panel |  | 45 |  | 45
44 | Blank panel |  | 44 |  | 44
43 | Blank panel |  | 43 |  | 43
42 | Blank panel |  | 42 |  | 42
41 | Blank panel |  | 41 |  | 41
40 | Blank panel |  | 40 |  | 40
39 | Blank panel |  | 39 |  | 39
38 | Blank panel |  | 38 |  | 38
37 | Blank panel |  | 37 |  | 37
36 | Blank panel |  | 36 |  | 36
35 | Blank panel |  | 35 |  | 35
34 | Blank panel |  | 34 |  | 34
33 | Blank panel |  | 33 |  | 33
32 | Blank panel |  | 32 |  | 32
31 | Blank panel |  | 31 |  | 31
30 | Blank panel |  | 30 |  | 30
29 | Blank panel |  | 29 |  | 29
28 | Blank panel |  | 28 |  | 28
27 | Blank panel |  | 27 |  | 27
26 | Blank panel |  | 26 |  | 26
25 | Blank panel |  | 25 |  | 25
24 | Blank panel |  | 24 |  | 24
23 | Blank panel |  | 23 |  | 23
22 | 2U Cables Passthrough (for Network Cables) |  | 22 |  | 22
21 |  |  | 21 |  | 21
20 | Spine Router B Cisco N9K-C9508 Chassis Ports Side |  | 20 | Spine Router B Cisco N9K-C9508 Chassis | 20
19 |  |  | 19 |  | 19
18 |  |  | 18 |  | 18
17 |  |  | 17 |  | 17
16 |  |  | 16 |  | 16
15 |  |  | 15 |  | 15
14 |  |  | 14 |  | 14
13 |  |  | 13 |  | 13
12 |  |  | 12 |  | 12
11 |  |  | 11 |  | 11
10 |  |  | 10 |  | 10
9 |  |  | 9 |  | 9
8 |  |  | 8 |  | 8
7 |  |  | 7 |  | 7
6 |  |  | 6 |  | 6
5 |  |  | 5 |  | 5
4 | 2U Cables Passthrough (for Power cords) |  | 4 |  | 4
3 |  |  | 3 |  | 3
2 | Blank panel |  | 2 |  | 2
1 | Blank panel |  | 1 |  | 1
https://example.com

## Rack-LF-A (503)
RU | Chassis Rack Layout - Front | PDU A | RU | Chassis Rack Layout - Rear |  | PDU B
48 | LC/LC Patch Panel Unidentified |  | 48 | LC/LC Patch Panel Unidentified (Rear) | 48
47 | Blank panel |  | 47 |  | 47
46 | Blank panel |  | 46 |  | 46
45 | Blank panel |  | 45 |  | 45
44 | Blank panel |  | 44 |  | 44
43 | Blank panel |  | 43 |  | 43
42 | Blank panel |  | 42 |  | 42
41 | Blank panel |  | 41 |  | 41
40 | Blank panel |  | 40 |  | 40
39 | Blank panel |  | 39 |  | 39
38 | Blank panel |  | 38 |  | 38
37 | Blank panel |  | 37 |  | 37
36 | Blank panel |  | 36 |  | 36
35 | Blank panel |  | 35 |  | 35
34 | Blank panel |  | 34 |  | 34
33 | Blank panel |  | 33 |  | 33
32 | Blank panel |  | 32 |  | 32
31 | Blank panel |  | 31 |  | 31
30 | Blank panel |  | 30 |  | 30
29 | Blank panel |  | 29 |  | 29
28 | Blank panel |  | 28 |  | 28
27 | Blank panel |  | 27 |  | 27
26 | Blank panel |  | 26 |  | 26
25 | Blank panel |  | 25 |  | 25
24 | Blank panel |  | 24 |  | 24
23 | Blank panel |  | 23 |  | 23
22 | 2U Cables Passthrough (for Network Cables) |  | 22 |  | 22
21 |  |  | 21 |  | 21
20 | Leaf Switch A Cisco N9K-C9508 Chassis Port Side |  | 20 | Leaf Switch A Cisco N9K-C9508 Chassis | 20
19 |  |  | 19 |  | 19
18 |  |  | 18 |  | 18
17 |  |  | 17 |  | 17
16 |  |  | 16 |  | 16
15 |  |  | 15 |  | 15
14 |  |  | 14 |  | 14
13 |  |  | 13 |  | 13
12 |  |  | 12 |  | 12
11 |  |  | 11 |  | 11
10 |  |  | 10 |  | 10
9 |  |  | 9 |  | 9
8 |  |  | 8 |  | 8
7 |  |  | 7 |  | 7
6 |  |  | 6 |  | 6
5 |  |  | 5 |  | 5
4 | 2U Cables Passthrough (for Power cords) |  | 4 |  | 4
3 |  |  | 3 |  | 3
2 | Blank panel |  | 2 |  | 2
1 | Blank panel |  | 1 |  | 1
https://example.com

## Rack-LF-B (504)
RU | Chassis Rack Layout - Front |  | PDU A | RU | Chassis Rack Layout - Rear | RU | PDU B
48 | LC/LC Patch Panel Unidentified | P1 going to Media Converter in rack 0501 |  | 48 | LC/LC Patch Panel Unidentified (Rear) | 48
47 | Blank panel |  |  | 47 |  | 47
46 | Blank panel |  |  | 46 |  | 46
45 | Blank panel |  |  | 45 |  | 45
44 | Blank panel |  |  | 44 |  | 44
43 | Blank panel |  |  | 43 |  | 43
42 | Blank panel |  |  | 42 |  | 42
41 | Blank panel |  |  | 41 |  | 41
40 | Blank panel |  |  | 40 |  | 40
39 | Blank panel |  |  | 39 |  | 39
38 | Blank panel |  |  | 38 |  | 38
37 | Blank panel |  |  | 37 |  | 37
36 | Blank panel |  |  | 36 |  | 36
35 | Blank panel |  |  | 35 |  | 35
34 | Blank panel |  |  | 34 |  | 34
33 | Blank panel |  |  | 33 |  | 33
32 | Blank panel |  |  | 32 |  | 32
31 | Blank panel |  |  | 31 |  | 31
30 | Blank panel |  |  | 30 |  | 30
29 | Blank panel |  |  | 29 |  | 29
28 | Blank panel |  |  | 28 |  | 28
27 | Blank panel |  |  | 27 |  | 27
26 | Blank panel |  |  | 26 |  | 26
25 | Blank panel |  |  | 25 |  | 25
24 | Blank panel |  |  | 24 |  | 24
23 | Blank panel |  |  | 23 |  | 23
22 | 2U Cables Passthrough (for Network Cables) |  |  | 22 |  | 22
21 |  |  |  | 21 |  | 21
20 | Leaf Switch B Cisco N9K-C9508 Chassis Port Side |  |  | 20 | Leaf Switch B Cisco N9K-C9508 Chassis | 20
19 |  |  |  | 19 |  | 19
18 |  |  |  | 18 |  | 18
17 |  |  |  | 17 |  | 17
16 |  |  |  | 16 |  | 16
15 |  |  |  | 15 |  | 15
14 |  |  |  | 14 |  | 14
13 |  |  |  | 13 |  | 13
12 |  |  |  | 12 |  | 12
11 |  |  |  | 11 |  | 11
10 |  |  |  | 10 |  | 10
9 |  |  |  | 9 |  | 9
8 |  |  |  | 8 |  | 8
7 |  |  |  | 7 |  | 7
6 |  |  |  | 6 |  | 6
5 |  |  |  | 5 |  | 5
4 | 2U Cables Passthrough (for Power cords) |  |  | 4 |  | 4
3 |  |  |  | 3 |  | 3
2 | Blank panel |  |  | 2 |  | 2
1 | Blank panel |  |  | 1 |  | 1
https://example.com

## Power Layout
PDU Whips Orientation ToR
R0501-SP-A (Spine Switch A) | Endpoints
| Device 1 |  |  | Device 2
| RU | PDU Name | PDU Receptacle | RU | Device Name | PSU | Cable Type | Cable Length | Cable Color | Notes | Label 1 | Label 2
| 0 | PDUA | 16 | 5 | Spine Router | 6-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 16 <-> RU5 PSU 6-A | RU5 PSU 6-A <-> PDUA Rec 16
| 0 | PDUA | 20 | 5 | Spine Router | 12-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 20 <-> RU5 PSU 12-A | RU5 PSU 12-A <-> PDUA Rec 20
| 0 | PDUA | 24 | 5 | Spine Router | 5-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 24 <-> RU5 PSU 5-A | RU5 PSU 5-A <-> PDUA Rec 24
| 0 | PDUA | 32 | 5 | Spine Router | 11-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 32 <-> RU5 PSU 11-A | RU5 PSU 11-A <-> PDUA Rec 32
| 0 | PDUA | 36 | 5 | Spine Router | 4-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 36 <-> RU5 PSU 4-A | RU5 PSU 4-A <-> PDUA Rec 36
| 0 | PDUA | 40 | 5 | Spine Router | 10-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 40 <-> RU5 PSU 10-A | RU5 PSU 10-A <-> PDUA Rec 40
| 0 | PDUA | 44 | 5 | Spine Router | 3-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 44 <-> RU5 PSU 3-A | RU5 PSU 3-A <-> PDUA Rec 44
| 0 | PDUA | 48 | 5 | Spine Router | 9-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 48 <-> RU5 PSU 9-A | RU5 PSU 9-A <-> PDUA Rec 48
| 0 | PDUA | 1 | 40 | Mgmt Switch | 1 | C15-14 |  |  | OEM supplied power cords | PDUA Rec 1 <-> RU40 PSU 1 | RU40 PSU 1 <-> PDUA Rec 1 | take from liquidation
| 0 | PDUA | 3 | 37 | Console Server | 1 | C13-14 |  |  | OEM supplied power cords | PDUA Rec 3 <-> RU37 PSU 1 | RU37 PSU 1 <-> PDUA Rec 3 | take from liquidation
| 0 | PDUB | 16 | 5 | Spine Router | 6-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 16 <-> RU5 PSU 6-B | RU5 PSU 6-B <-> PDUB Rec 16
| 0 | PDUB | 20 | 5 | Spine Router | 12-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 20 <-> RU5 PSU 12-B | RU5 PSU 12-B <-> PDUB Rec 20
| 0 | PDUB | 24 | 5 | Spine Router | 5-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 24 <-> RU5 PSU 5-B | RU5 PSU 5-B <-> PDUB Rec 24
| 0 | PDUB | 32 | 5 | Spine Router | 11-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 32 <-> RU5 PSU 11-B | RU5 PSU 11-B <-> PDUB Rec 32
| 0 | PDUB | 36 | 5 | Spine Router | 4-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 36 <-> RU5 PSU 4-B | RU5 PSU 4-B <-> PDUB Rec 36
| 0 | PDUB | 40 | 5 | Spine Router | 10-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 40 <-> RU5 PSU 10-B | RU5 PSU 10-B <-> PDUB Rec 40
| 0 | PDUB | 44 | 5 | Spine Router | 3-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 44 <-> RU5 PSU 3-B | RU5 PSU 3-B <-> PDUB Rec 44
| 0 | PDUB | 48 | 5 | Spine Router | 9-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 48 <-> RU5 PSU 9-B | RU5 PSU 9-B <-> PDUB Rec 48
| 0 | PDUB | 1 | 40 | Mgmt Switch | 2 | C15-14 |  |  | OEM supplied power cords | PDUB Rec 1 <-> RU40 PSU 2 | RU40 PSU 2 <-> PDUB Rec 1 | take from liquidation
| 0 | PDUB | 3 | 37 | Console Server | 2 | C13-14 |  |  | OEM supplied power cords | PDUB Rec 3 <-> RU37 PSU 2 | RU37 PSU 2 <-> PDUB Rec 3 | take from liquidation
| 0 | PDUB | 7 | 39 | TP-Link Media Converter | TP-Link | AC-DC adapter to C14 to 5-15R |  |  | OEM supplied power cords | PDUB Rec 7 <-> RU39 TP-Link | RU39 TP-Link <-> PDUB Rec 7
PDU Whips Orientation ToR
R0502-SP-B (cloud Edge B) | Endpoints
| Device 1 |  |  | Device 2
| RU | PDU Name | PDU Receptacle | RU | Device Name | PSU | Cable Type | Cable Length | Cable Color | Notes | Label 1 | Label 2
| 0 | PDUA | 16 | 5 | Spine Router | 6-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 16 <-> RU5 PSU 6-A | RU5 PSU 6-A <-> PDUA Rec 16
| 0 | PDUA | 20 | 5 | Spine Router | 12-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 20 <-> RU5 PSU 12-A | RU5 PSU 12-A <-> PDUA Rec 20
| 0 | PDUA | 24 | 5 | Spine Router | 5-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 24 <-> RU5 PSU 5-A | RU5 PSU 5-A <-> PDUA Rec 24
| 0 | PDUA | 32 | 5 | Spine Router | 11-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 32 <-> RU5 PSU 11-A | RU5 PSU 11-A <-> PDUA Rec 32
| 0 | PDUA | 36 | 5 | Spine Router | 4-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 36 <-> RU5 PSU 4-A | RU5 PSU 4-A <-> PDUA Rec 36
| 0 | PDUA | 40 | 5 | Spine Router | 10-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 40 <-> RU5 PSU 10-A | RU5 PSU 10-A <-> PDUA Rec 40
| 0 | PDUA | 44 | 5 | Spine Router | 3-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 44 <-> RU5 PSU 3-A | RU5 PSU 3-A <-> PDUA Rec 44
| 0 | PDUA | 48 | 5 | Spine Router | 9-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 48 <-> RU5 PSU 9-A | RU5 PSU 9-A <-> PDUA Rec 48
| 0 | PDUB | 16 | 5 | Spine Router | 6-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 16 <-> RU5 PSU 6-B | RU5 PSU 6-B <-> PDUB Rec 16
| 0 | PDUB | 20 | 5 | Spine Router | 12-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 20 <-> RU5 PSU 12-B | RU5 PSU 12-B <-> PDUB Rec 20
| 0 | PDUB | 24 | 5 | Spine Router | 5-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 24 <-> RU5 PSU 5-B | RU5 PSU 5-B <-> PDUB Rec 24
| 0 | PDUB | 32 | 5 | Spine Router | 11-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 32 <-> RU5 PSU 11-B | RU5 PSU 11-B <-> PDUB Rec 32
| 0 | PDUB | 36 | 5 | Spine Router | 4-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 36 <-> RU5 PSU 4-B | RU5 PSU 4-B <-> PDUB Rec 36
| 0 | PDUB | 40 | 5 | Spine Router | 10-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 40 <-> RU5 PSU 10-B | RU5 PSU 10-B <-> PDUB Rec 40
| 0 | PDUB | 44 | 5 | Spine Router | 3-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 44 <-> RU5 PSU 3-B | RU5 PSU 3-B <-> PDUB Rec 44
| 0 | PDUB | 48 | 5 | Spine Router | 9-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 48 <-> RU5 PSU 9-B | RU5 PSU 9-B <-> PDUB Rec 48
PDU Whips Orientation ToR
R0503-LF-A (Leaf Switch A) | Endpoints
| Device 1 |  |  | Device 2
| RU | PDU Name | PDU Receptacle | RU | Device Name | PSU | Cable Type | Cable Length | Cable Color | Notes | Label 1 | Label 2
| 0 | PDUA | 16 | 5 | Spine Router | 6-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 16 <-> RU5 PSU 6-A | RU5 PSU 6-A <-> PDUA Rec 16
| 0 | PDUA | 20 | 5 | Spine Router | 12-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 20 <-> RU5 PSU 12-A | RU5 PSU 12-A <-> PDUA Rec 20
| 0 | PDUA | 24 | 5 | Spine Router | 5-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 24 <-> RU5 PSU 5-A | RU5 PSU 5-A <-> PDUA Rec 24
| 0 | PDUA | 32 | 5 | Spine Router | 11-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 32 <-> RU5 PSU 11-A | RU5 PSU 11-A <-> PDUA Rec 32
| 0 | PDUA | 36 | 5 | Spine Router | 4-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 36 <-> RU5 PSU 4-A | RU5 PSU 4-A <-> PDUA Rec 36
| 0 | PDUA | 40 | 5 | Spine Router | 10-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 40 <-> RU5 PSU 10-A | RU5 PSU 10-A <-> PDUA Rec 40
| 0 | PDUA | 44 | 5 | Spine Router | 3-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 44 <-> RU5 PSU 3-A | RU5 PSU 3-A <-> PDUA Rec 44
| 0 | PDUA | 48 | 5 | Spine Router | 9-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 48 <-> RU5 PSU 9-A | RU5 PSU 9-A <-> PDUA Rec 48
| 0 | PDUB | 16 | 5 | Spine Router | 6-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 16 <-> RU5 PSU 6-B | RU5 PSU 6-B <-> PDUB Rec 16
| 0 | PDUB | 20 | 5 | Spine Router | 12-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 20 <-> RU5 PSU 12-B | RU5 PSU 12-B <-> PDUB Rec 20
| 0 | PDUB | 24 | 5 | Spine Router | 5-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 24 <-> RU5 PSU 5-B | RU5 PSU 5-B <-> PDUB Rec 24
| 0 | PDUB | 32 | 5 | Spine Router | 11-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 32 <-> RU5 PSU 11-B | RU5 PSU 11-B <-> PDUB Rec 32
| 0 | PDUB | 36 | 5 | Spine Router | 4-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 36 <-> RU5 PSU 4-B | RU5 PSU 4-B <-> PDUB Rec 36
| 0 | PDUB | 40 | 5 | Spine Router | 10-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 40 <-> RU5 PSU 10-B | RU5 PSU 10-B <-> PDUB Rec 40
| 0 | PDUB | 44 | 5 | Spine Router | 3-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 44 <-> RU5 PSU 3-B | RU5 PSU 3-B <-> PDUB Rec 44
| 0 | PDUB | 48 | 5 | Spine Router | 9-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 48 <-> RU5 PSU 9-B | RU5 PSU 9-B <-> PDUB Rec 48
PDU Whips Orientation ToR
R0504-LF-B (Leaf Switch B) | Endpoints
| Device 1 |  |  | Device 2
| RU | PDU Name | PDU Receptacle | RU | Device Name | PSU | Cable Type | Cable Length | Cable Color | Notes | Label 1 | Label 2
| 0 | PDUA | 16 | 5 | Spine Router | 6-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 16 <-> RU5 PSU 6-A | RU5 PSU 6-A <-> PDUA Rec 16
| 0 | PDUA | 20 | 5 | Spine Router | 12-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 20 <-> RU5 PSU 12-A | RU5 PSU 12-A <-> PDUA Rec 20
| 0 | PDUA | 24 | 5 | Spine Router | 5-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 24 <-> RU5 PSU 5-A | RU5 PSU 5-A <-> PDUA Rec 24
| 0 | PDUA | 32 | 5 | Spine Router | 11-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 32 <-> RU5 PSU 11-A | RU5 PSU 11-A <-> PDUA Rec 32
| 0 | PDUA | 36 | 5 | Spine Router | 4-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 36 <-> RU5 PSU 4-A | RU5 PSU 4-A <-> PDUA Rec 36
| 0 | PDUA | 40 | 5 | Spine Router | 10-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 40 <-> RU5 PSU 10-A | RU5 PSU 10-A <-> PDUA Rec 40
| 0 | PDUA | 44 | 5 | Spine Router | 3-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 44 <-> RU5 PSU 3-A | RU5 PSU 3-A <-> PDUA Rec 44
| 0 | PDUA | 48 | 5 | Spine Router | 9-A | C20-Anderson |  |  | OEM supplied power cords | PDUA Rec 48 <-> RU5 PSU 9-A | RU5 PSU 9-A <-> PDUA Rec 48
| 0 | PDUB | 16 | 5 | Spine Router | 6-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 16 <-> RU5 PSU 6-B | RU5 PSU 6-B <-> PDUB Rec 16
| 0 | PDUB | 20 | 5 | Spine Router | 12-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 20 <-> RU5 PSU 12-B | RU5 PSU 12-B <-> PDUB Rec 20
| 0 | PDUB | 24 | 5 | Spine Router | 5-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 24 <-> RU5 PSU 5-B | RU5 PSU 5-B <-> PDUB Rec 24
| 0 | PDUB | 32 | 5 | Spine Router | 11-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 32 <-> RU5 PSU 11-B | RU5 PSU 11-B <-> PDUB Rec 32
| 0 | PDUB | 36 | 5 | Spine Router | 4-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 36 <-> RU5 PSU 4-B | RU5 PSU 4-B <-> PDUB Rec 36
| 0 | PDUB | 40 | 5 | Spine Router | 10-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 40 <-> RU5 PSU 10-B | RU5 PSU 10-B <-> PDUB Rec 40
| 0 | PDUB | 44 | 5 | Spine Router | 3-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 44 <-> RU5 PSU 3-B | RU5 PSU 3-B <-> PDUB Rec 44
| 0 | PDUB | 48 | 5 | Spine Router | 9-B | C20-Anderson |  |  | OEM supplied power cords | PDUB Rec 48 <-> RU5 PSU 9-B | RU5 PSU 9-B <-> PDUB Rec 48
PDU whips orientation ToR
[13 empty] | C Breaker1 | L1 | 2 | 1
[15 empty] | 4 | 3
[13 empty] | C Breaker2 | L2 | 6 | 5
[15 empty] | 8 | 7
[13 empty] | C Breaker3 | L3 | 10 | 9
[15 empty] | 12 | 11
[13 empty] | C Breaker1 | L1 | 14 | 13
[15 empty] | 16 | 15
[13 empty] | C Breaker2 | L2 | 18 | 17
[15 empty] | 20 | 19
[13 empty] | C Breaker3 | L3 | 22 | 21
[15 empty] | 24 | 23
[13 empty] | C Breaker4 | L1 | 26 | 25
[15 empty] | 28 | 27
[13 empty] | C Breaker5 | L2 | 30 | 29
[15 empty] | 32 | 31
[13 empty] | C Breaker6 | L3 | 34 | 33
[15 empty] | 36 | 35
[13 empty] | C Breaker4 | L1 | 38 | 37
[15 empty] | 40 | 39
[13 empty] | C Breaker5 | L2 | 42 | 41
[15 empty] | 44 | 43
[13 empty] | C Breaker6 | L3 | 46 | 45
[15 empty] | 48 | 47

## BOM
Item # | Manufacturer | Part # | Product ID | Product | Quantity Per Rack | Quantity per Site
Cisco Network Chassis
1 | Cisco Systems | N9K-C9508-B3 |  | 1 Cisco Nexus 9508 Chassis bundle. Includes N9K-C9508 chassis, 8x3kW AC PS, 6xFM-E2, 2xSUP-A+, (Extended Rack Kit) Cisco Systems - Part#: N9K-C9508-B3 | 1 | 4
2 | Cisco Systems | N9K-X9736C-FX |  | 1-800-200-0001 Series 36 port 400GbE QSFP-DD line card with MACsec and Large Route Scale Cisco Systems - Part#: N9K-X9736C-FX | 2 | 8
3 | Cisco Systems | NXOS-ESS-XF |  | 3 NX-OS Essentials License for Nexus 9500 Modular Switches (OSPF, BGP, VXLAN) Cisco Systems - Part#: NXOS-ESS-XF | 1 | 4
4 | Cisco Systems | NXOS-ADV-XF |  | 4 NX-OS Advantage License for Nexus 9500 (Analytics, Telemetry, ACI) Cisco Systems - Part#: NXOS-ADV-XF | 1 | 4
5 | Cisco Systems | DNA-SW-SUB-1M |  | 5 DNA Center SW Subscription License 1-Month for Modular Switches Cisco - Part#: DNA-SW-SUB-1M Note: Term: 36 months | 1 | 4
6 | Cisco Systems | CON-SNT-N9K508 |  | 6 1-Month SmartNet 8x5xNBD Hardware Replacement for N9K-C9508 Cisco Systems - Part#: CON-SNT-N9K508 Note: Term: 36 months | 1 | 4
7 | Cisco Systems | N9K-SUP-A+ |  | Cisco N9K-SUP-A+ Supervisor module for Nexus 9500 series with enhanced forwarding | 1 | 4 | Potentialy Moving to SUP2
8 | Cisco Systems | QSFP-100G-AOC7M |  | 9 100G QSFP28 to QSFP28 Active Optical Cable, 7 meter Cisco - Part#: QSFP-100G-AOC7M |  | 12 | 2 spares
9 | Cisco Systems | QSFP-100G-AOC10M |  | 10 100G QSFP28 to QSFP28 Active Optical Cable, 10 meter Cisco - Part#: QSFP-100G-AOC10M |  | 28 | 2 spares
10 | CommScope | 3M-2FSM-LCLC-CS |  | OS2 LC-LC Duplex SMF fiber cable 3 meters |  | 56 | extra 12 cables
11 | General | CAT6 patch copper cables Blue 1.5M |  | CAT6 patch copper cables Blue 1.5Meters |  | 1
12 | General | CAT6 patch copper cables Blue 3M |  | CAT6 patch copper cables Blue 3Meters (10FT) |  | 6
13 | General | CAT6 patch copper cables Blue 7M |  | CAT6 patch copper cables Blue 7Meters (23FT) |  | 6
14 | General | CAT6 patch copper cables Blue 10M |  | CAT6 patch copper cables Blue 10Meters (35 FT) |  | 12
Cabinet and PDUs
15 | Panduit | N8222BC | 58473921 | Panduit Net-Access Rack - 2200H x 800W x 1070D mm, with Sides - floor-standing - black - 45U - 19" - TAA Compliant | 1 | 4
16 | Panduit | PBDK-45 | 47291836 | Panduit High Seismic Bolt-Down Kit for 45U Racks - black | 1 | 4
17 | APC by Schneider Electric | AR7711 | 17963815 | APC NetShelter Zero U - Rack mounting kit - 0U - for P/N: SNBB682575EC87, SNA171AC, SN826A6FCE48, SN478DCB74F213, SMX750C, SN45D2CCE | 1 | 4
18 | APC by Schneider Electric | SN8038A39D5 |  | APC NetShelter Rack PDU Advanced - Gen 2 - power distribution unit (rack-mountable) - switched, 22.1kW, 400V, 32A, or, 415V, 30A, 530P6 - AC 400/415 V - 17.3 kW - 17300 VA - 3-phase - Ethernet 10/100/1000, USB - input: IEC 60309 3P+N+PE - output | 2 | 8
19 | FS.COM | 1U Horizontal Cable manager |  | 1U Horizontal Cable manager |  | 2
20 | Cisco | CCS-720XP-48TXH-2C-S-5G-2F |  | Cisco 720XP, 48 x 5G, 90W POE, 4x25G SFP28, 2x100G QSFP switch, front to rear air, AC |  | 1
21 | OpenGear | OPE-CM8196-10G |  | 96 selectable serial ports, 2x 10GbE SFP+, 2x 1GbE, 2 x USB 3.0 host ports, 1 x RJ45 RS-232 Console Port, ARM 1.6GHz 2-core 2GB mem 32GB flash, TPM 2.0, Docker support, 2RU, Dual AC, C14 power cord |  | 1 | Customer provided
22 | SNE0853964 | 712774 |  | 2U INT Cable Entry panel w/brush | 2 | 8
23 | Proficium Inc. | HLR.5X25BK |  | 1/2IN H&L Wrap-25yd Black |  | 4
24 | Proficium | SL500-BK-100 |  | 1/2IN Splt Lm PE Black 100FT |  | 1
25 | FS.COM Media Converter | FS.COM Media Converter |  | FS.COM media Converter |  | 1 | Customer provided
26 | General | C14_5-15R Adapter |  | C14 to 5-15R power adapter |  | 1
27 | General | C14-C15 |  | C14-C15 Power cord 6FT Black |  | 2
28 | Cisco | OSFP 2×FR4-800G |  | 2x SNB50AF0-FR4 / SN3B9717-FR4 Dual-Rate Transceiver, dual LC connectors, up to 2km over dual duplex SMF. Interoperates with 2x 400G-FR4 OSFP / QSFPDD, or 2x 200G-FR4 QSFPs. |  | 24 | 8 spares
29 | Cisco | ADPT-O-Q-100G |  | OSFP to 100G QSFP adapter |  | 5
30 | Cisco | OSFP-800G-2XDR |  | 2x SN22F244-XDR4 Transceiver, Dual MPO-12 APC connector, 2km over parallel SMF. Interoperates with 2x 400G-XDR4 OSFP / QSFP-DD, and 8x 100G-FR QSFPs. |  | 2
31 | Cisco | 10GBASE-LR |  | Up to 10km link length over duplex single-mode fiber. |  | 2
32 | General | MPO- 4 x LC-SMF-3M |  | MPO to 4x LCs breakout cables SMF fiber cable (3meter) |  | 2 | Not used
33 | Cisco | OSFP-400G-LR4 |  | Cisco Systems OSFP-400G-LR4 Compatible SNF58D66-LR4 OSFP Finned Top PAM4 1310nm 10km DOM Duplex LC/UPC SMF Optical Transceiver Module |  | 16
34 | Cisco | QSFP-100G-LR4 |  | Cisco Systems QSFP-100G-LR4 Compatible SN9CBEE3-LR4 QSFP28 Optical Transceiver Module (SMF, 1310nm, 10km, LC, DOM) |  | 5

## Fiber panels Network Layout
Make/Model | Rack | *RU | *Device Name | Module # | Slot/Port # | port port position | Optic | Cable Type | Length | PP Side | <------> | *RU | *VIA-PP | Tray # | *VIA-Port | VIA-Cable Type | PP Side | <------> Length | PP Side | *RU | *VIA-PP | *VIA-Port | VIA-Cable Type | <------> | PP Side | Make/Model | Rack | *RU | *Device Name | *Port | Optic | Cable Type | Length | Notes
From Device being Installed Information | [11 empty] | Fiber Panels | [12 empty] | To Device being Installed Information
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 13 | 1 | QSFP56-DD-400G | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m1/17/1 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 13 | 5 |  | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m1/17/5 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 14 | 1 | QSFP56-DD-400G | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m1/18/1 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 14 | 5 |  | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m1/18/5 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 15 | 1 | QSFP56-DD-400G | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m1/19/1 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 15 | 5 |  | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m1/19/5 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 16 | 1 | QSFP56-DD-400G | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m1/20/1 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 16 | 5 |  | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m1/20/5 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 19 | 1 | 100G QSFP LRF4 via OSFP-QSFP28 Adapter | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m1/19/1 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 20 | 1 | 100G QSFP LRF4 via OSFP-QSFP28 Adapter | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m1/20/1 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 13 | 1 | QSFP56-DD-400G | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m2/17/1 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 13 | 5 |  | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m2/17/5 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 14 | 1 | QSFP56-DD-400G | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m2/18/1 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 14 | 5 |  | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m2/18/5 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 15 | 1 | QSFP56-DD-400G | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m2/19/1 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 15 | 5 |  | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m2/19/5 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 16 | 1 | QSFP56-DD-400G | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m2/20/1 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 16 | 5 |  | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m2/20/5 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 19 | 1 | 100G QSFP LRF4 via OSFP-QSFP28 Adapter | LC-LC SMF Duplex | 3m | Front | R0501-SP-A RU5 m2/19/1 <-> R0501-SP-A RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 13 | 1 | QSFP56-DD-400G | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m1/17/1 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 13 | 5 |  | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m1/17/5 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 14 | 1 | QSFP56-DD-400G | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m1/18/1 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 14 | 5 |  | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m1/18/5 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 15 | 1 | QSFP56-DD-400G | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m1/19/1 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 15 | 5 |  | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m1/19/5 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 16 | 1 | QSFP56-DD-400G | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m1/20/1 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 16 | 5 |  | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m1/20/5 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 19 | 1 | 100G QSFP LRF4 via OSFP-QSFP28 Adapter | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m1/19/1 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 20 | 1 | 100G QSFP LRF4 via OSFP-QSFP28 Adapter | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m1/20/1 <-> R0502-SP-B RU47 : | 47 | SP-A-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 13 | 1 | QSFP56-DD-400G | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m2/17/1 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 13 | 5 |  | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m2/17/5 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 14 | 1 | QSFP56-DD-400G | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m2/18/1 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 14 | 5 |  | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m2/18/5 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 15 | 1 | QSFP56-DD-400G | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m2/19/1 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 15 | 5 |  | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m2/19/5 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 16 | 1 | QSFP56-DD-400G | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m2/20/1 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 16 | 5 |  | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m2/20/5 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 19 | 1 | 100G QSFP LRF4 via OSFP-QSFP28 Adapter | LC-LC SMF Duplex | 3m | Front | R0502-SP-B RU5 m2/19/1 <-> R0502-SP-B RU47 : | 47 | CE-B-PP2 |  |  | LC/LC Duplex | Rear
1Ux 24x 1G mgmt SW | R0502-SP-B | 40 | OOB Mgmt Switch |  | 49 |  | LR SFP | LC-LC SMF Duplex | 3m |  | R0502-SP-B RU40 P49 <-> R0502-SP-B RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex
1Ux 24x 1G mgmt SW | R0502-SP-B | 40 | OOB Mgmt Switch |  | 50 |  | LR SFP | LC-LC SMF Duplex | 3m |  | R0502-SP-B RU40 P50 <-> R0502-SP-B RU47 : | 47 | SP-A-PP1 |  |  | LC/LC Duplex

## Network Layout
Source Device | [6 empty] | Label | Destination Device
Make/Model | Rack | *RU | *Device Name | Module # | *Port | Optic | <------> | Make/Model | Rack | *RU | *Device Name | Module # | *Port | Optic | Cable Type | Length | Cable Color | Notes
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 1 | N/A | R0501-SP-A RU5 m1/9 <-> R0503-LF-A RU5 m1/9 | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m1 | 1 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 2 | N/A | R0501-SP-A RU5 m1/10 <-> R0503-LF-A RU5 m1/10 | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m1 | 2 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 3 | N/A | R0501-SP-A RU5 m1/11 <-> R0503-LF-A RU5 m1/11 | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m1 | 3 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 4 | N/A | R0501-SP-A RU5 m1/12 <-> R0503-LF-A RU5 m1/12 | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m1 | 4 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 5 | N/A | R0501-SP-A RU5 m1/9 <-> R0503-LF-A RU5 m1/9 | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m1 | 5 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 6 | N/A | R0501-SP-A RU5 m1/10 <-> R0503-LF-A RU5 m1/10 | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m1 | 6 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 7 | N/A | R0501-SP-A RU5 m1/11 <-> R0503-LF-A RU5 m1/11 | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m1 | 7 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m1 | 8 | N/A | R0501-SP-A RU5 m1/12 <-> R0503-LF-A RU5 m1/12 | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m1 | 8 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 1 | N/A | R0501-SP-A RU5 m2/9 <-> R0504-LF-B RU5 m2/9 | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m2 | 1 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 2 | N/A | R0501-SP-A RU5 m2/10 <-> R0504-LF-B RU5 m2/10 | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m2 | 2 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 3 | N/A | R0501-SP-A RU5 m2/11 <-> R0504-LF-B RU5 m2/11 | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m2 | 3 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 4 | N/A | R0501-SP-A RU5 m2/12 <-> R0504-LF-B RU5 m2/12 | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m2 | 4 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 5 | N/A | R0501-SP-A RU5 m2/9 <-> R0504-LF-B RU5 m2/9 | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m2 | 5 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 6 | N/A | R0501-SP-A RU5 m2/10 <-> R0504-LF-B RU5 m2/10 | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m2 | 6 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 7 | N/A | R0501-SP-A RU5 m2/11 <-> R0504-LF-B RU5 m2/11 | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m2 | 7 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | m2 | 8 | N/A | R0501-SP-A RU5 m2/12 <-> R0504-LF-B RU5 m2/12 | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m2 | 8 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
Ports 9 to 12 reserved on both linecards
|  | 5 |  |  |  |  | RU5 / <-> RU5 / |  |  | 5 | [8 empty] | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 1 | N/A | R0502-SP-B RU5 m1/9 <-> R0504-LF-B RU5 m1/9 | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m1 | 1 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 2 | N/A | R0502-SP-B RU5 m1/10 <-> R0504-LF-B RU5 m1/10 | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m1 | 2 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 3 | N/A | R0502-SP-B RU5 m1/11 <-> R0504-LF-B RU5 m1/11 | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m1 | 3 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 4 | N/A | R0502-SP-B RU5 m1/12 <-> R0504-LF-B RU5 m1/12 | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m1 | 4 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 5 | N/A | R0502-SP-B RU5 m1/9 <-> R0504-LF-B RU5 m1/9 | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m1 | 5 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 6 | N/A | R0502-SP-B RU5 m1/10 <-> R0504-LF-B RU5 m1/10 | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m1 | 6 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 7 | N/A | R0502-SP-B RU5 m1/11 <-> R0504-LF-B RU5 m1/11 | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m1 | 7 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m1 | 8 | N/A | R0502-SP-B RU5 m1/12 <-> R0504-LF-B RU5 m1/12 | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m1 | 8 | N/A | QSFP-DD AOC | 10M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 1 | N/A | R0502-SP-B RU5 m2/9 <-> R0503-LF-A RU5 m2/9 | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m2 | 1 | N/A | QSFP-DD AOC | 7M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 2 | N/A | R0502-SP-B RU5 m2/10 <-> R0503-LF-A RU5 m2/10 | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m2 | 2 | N/A | QSFP-DD AOC | 7M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 3 | N/A | R0502-SP-B RU5 m2/11 <-> R0503-LF-A RU5 m2/11 | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m2 | 3 | N/A | QSFP-DD AOC | 7M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 4 | N/A | R0502-SP-B RU5 m2/12 <-> R0503-LF-A RU5 m2/12 | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m2 | 4 | N/A | QSFP-DD AOC | 7M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 5 | N/A | R0502-SP-B RU5 m2/9 <-> R0503-LF-A RU5 m2/9 | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m2 | 5 | N/A | QSFP-DD AOC | 7M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 6 | N/A | R0502-SP-B RU5 m2/10 <-> R0503-LF-A RU5 m2/10 | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m2 | 6 | N/A | QSFP-DD AOC | 7M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 7 | N/A | R0502-SP-B RU5 m2/11 <-> R0503-LF-A RU5 m2/11 | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m2 | 7 | N/A | QSFP-DD AOC | 7M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | m2 | 8 | N/A | R0502-SP-B RU5 m2/12 <-> R0503-LF-A RU5 m2/12 | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m2 | 8 | N/A | QSFP-DD AOC | 7M |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
Ports 9 to 12 reserved on both linecards
|  | 5 |  |  |  |  | RU5 / <-> RU / | [11 empty] | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m1 | 17 | QSFP28-100G-LR4 | R0503-LF-A RU5 m1/25 <-> Metro Ethernet Circuit 1 | Metro Ethernet Circuit 1 | [10 empty] | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m1 | 18 | QSFP28-100G-LR4 | R0503-LF-A RU5 m1/26 <-> Metro Ethernet Circuit 2 | Metro Ethernet Circuit 2 | [10 empty] | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m2 | 17 | QSFP28-100G-LR4 | R0503-LF-A RU5 m2/25 <-> Metro Ethernet Circuit 3 | Metro Ethernet Circuit 3 | [10 empty] | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | m2 | 18 | QSFP28-100G-LR4 | R0503-LF-A RU5 m2/26 <-> Metro Ethernet Circuit 4 | Metro Ethernet Circuit 4 | [10 empty] | The labels will be source / Destination in one side and Destination /Source in the other.
The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m1 | 17 | QSFP28-100G-LR4 | R0504-LF-B RU5 m1/25 <-> Metro Ethernet Circuit 5 | Metro Ethernet Circuit 5 | [10 empty] | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m1 | 18 | QSFP28-100G-LR4 | R0504-LF-B RU5 m1/26 <-> Metro Ethernet Circuit 6 | Metro Ethernet Circuit 6 | [10 empty] | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m2 | 17 | QSFP28-100G-LR4 | R0504-LF-B RU5 m2/25 <-> Metro Ethernet Circuit 7 | Metro Ethernet Circuit 7 | [10 empty] | The labels will be source / Destination in one side and Destination /Source in the other.
N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | m2 | 18 | QSFP28-100G-LR4 | R0504-LF-B RU5 m2/26 <-> Metro Ethernet Circuit 8 | Metro Ethernet Circuit 8 | [10 empty] | The labels will be source / Destination in one side and Destination /Source in the other.
The labels will be source / Destination in one side and Destination /Source in the other.
1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch |  | Eth1/9 | N/A | R0501-SP-A RU40 Eth1/9 <-> R0501-SP-A RU5 sup1/Mgmt | N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | sup1 | Mgmt | N/A | CAT6 | 10FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch |  | Eth1/10 | N/A | R0501-SP-A RU40 Eth1/10 <-> R0502-SP-B RU5 sup1/Mgmt | N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | sup1 | Mgmt | N/A | CAT6 | 23FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch |  | Eth1/11 | N/A | R0501-SP-A RU40 Eth1/11 <-> R0503-LF-A RU5 sup1/Mgmt | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | sup1 | Mgmt | N/A | CAT6 | 33FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch |  | Eth1/12 | N/A | R0501-SP-A RU40 Eth1/12 <-> R0504-LF-B RU5 sup1/Mgmt | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | sup1 | Mgmt | N/A | CAT6 | 33FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch |  | Eth1/16 | N/A | R0501-SP-A RU40 Eth1/16 <-> R0501-SP-A RU5 sup2/Mgmt | N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | sup2 | Mgmt | N/A | CAT6 | 10FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch |  | Eth1/25 | N/A | R0501-SP-A RU40 Eth1/25 <-> R0502-SP-B RU5 sup2/Mgmt | N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | sup2 | Mgmt | N/A | CAT6 | 23FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch |  | Eth1/26 | N/A | R0501-SP-A RU40 Eth1/26 <-> R0503-LF-A RU5 sup2/Mgmt | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | sup2 | Mgmt | N/A | CAT6 | 33FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch |  | Eth1/19 | N/A | R0501-SP-A RU40 Eth1/19 <-> R0504-LF-B RU5 sup2/Mgmt | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | sup2 | Mgmt | N/A | CAT6 | 33FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch |  | Eth1/12 | N/A | R0501-SP-A RU40 Eth1/12 <-> R0501-SP-A PDUA Mgmt | PDUA | R0501-SP-A | PDUA | PDUA |  | Mgmt | N/A | CAT6 | 10FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch |  | Eth1/9 | N/A | R0501-SP-A RU40 Eth1/9 <-> R0501-SP-A PDUB Mgmt | PDUB | R0501-SP-A | PDUB | PDUB |  | Mgmt | N/A | CAT6 | 10FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch |  | Eth1/10 | N/A | R0501-SP-A RU40 Eth1/10 <-> R0502-SP-B PDUA Mgmt | PDUA | R0502-SP-B | PDUA | PDUA |  | Mgmt | N/A | CAT6 | 23FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch |  | Eth1/11 | N/A | R0501-SP-A RU40 Eth1/11 <-> R0502-SP-B PDUB Mgmt | PDUB | R0502-SP-B | PDUB | PDUB |  | Mgmt | N/A | CAT6 | 23FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch |  | Eth1/12 | N/A | R0501-SP-A RU40 Eth1/12 <-> R0503-LF-A PDUA Mgmt | PDUA | R0503-LF-A | PDUA | PDUA |  | Mgmt | N/A | CAT6 | 33FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch |  | Eth1/13 | N/A | R0501-SP-A RU40 Eth1/13 <-> R0503-LF-A PDUB Mgmt | PDUB | R0503-LF-A | PDUB | PDUB |  | Mgmt | N/A | CAT6 | 33FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch |  | Eth1/14 | N/A | R0501-SP-A RU40 Eth1/14 <-> R0504-LF-B PDUA Mgmt | PDUA | R0504-LF-B | PDUA | PDUA |  | Mgmt | N/A | CAT6 | 33FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch |  | Eth1/15 | N/A | R0501-SP-A RU40 Eth1/15 <-> R0504-LF-B PDUB Mgmt | PDUB | R0504-LF-B | PDUB | PDUB |  | Mgmt | N/A | CAT6 | 33FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
The labels will be source / Destination in one side and Destination /Source in the other.
OpenGear | R0501-SP-A | 37 | Console Server |  | Eth1 | N/A | R0501-SP-A RU37 Eth1 <-> R0501-SP-A RU5 sup1/Console | N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | sup1 | Console | N/A | CAT6 | 10FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
OpenGear | R0501-SP-A | 37 | Console Server |  | Eth2 | N/A | R0501-SP-A RU37 Eth2 <-> R0502-SP-B RU5 sup1/Console | N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | sup1 | Console | N/A | CAT6 | 23FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
OpenGear | R0501-SP-A | 37 | Console Server |  | Eth6 | N/A | R0501-SP-A RU37 Eth6 <-> R0501-SP-A RU5 sup2/Console | N9K-C9508 | R0501-SP-A | 5 | Spine Switch A | sup2 | Console | N/A | CAT6 | 10FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
OpenGear | R0501-SP-A | 37 | Console Server |  | Eth7 | N/A | R0501-SP-A RU37 Eth7 <-> R0502-SP-B RU5 sup2/Console | N9K-C9508 | R0502-SP-B | 5 | Spine Switch B | sup2 | Console | N/A | CAT6 | 23FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
OpenGear | R0501-SP-A | 37 | Console Server |  | Eth3 | N/A | R0501-SP-A RU37 Eth3 <-> R0501-SP-A RU40 Console | 1Ux 24x 1G mgmt SW | R0501-SP-A | 40 | OOB Mgmt Switch A |  | Console | N/A | CAT6 | 5FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
OpenGear | R0501-SP-A | 37 | Console Server |  | Eth4 | N/A | R0501-SP-A RU37 Eth4 <-> R0503-LF-A RU5 sup1/Console | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | sup1 | Console | N/A | CAT6 | 33FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
OpenGear | R0501-SP-A | 37 | Console Server |  | Eth5 | N/A | R0501-SP-A RU37 Eth5 <-> R0504-LF-B RU5 sup1/Console | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | sup1 | Console | N/A | CAT6 | 33FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
OpenGear | R0501-SP-A | 37 | Console Server |  | Eth8 | N/A | R0501-SP-A RU37 Eth8 <-> R0503-LF-A RU5 sup2/Console | N9K-C9508 | R0503-LF-A | 5 | Leaf Switch A | sup2 | Console | N/A | CAT6 | 33FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
OpenGear | R0501-SP-A | 37 | Console Server |  | Eth9 | N/A | R0501-SP-A RU37 Eth9 <-> R0504-LF-B RU5 sup2/Console | N9K-C9508 | R0504-LF-B | 5 | Leaf Switch B | sup2 | Console | N/A | CAT6 | 33FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
OpenGear | R0501-SP-A | 37 | Console Server |  | NET3 | N/A | R0501-SP-A RU37 NET3 <-> R0501-SP-A RU39 | TP-Link | R0501-SP-A | 39 | TP-Link Media Converter |  |  | N/A | CAT6 | 5FT |  |  | The labels will be source / Destination in one side and Destination /Source in the other.
TP-Link | R0501-SP-A | 39 | TP-Link Media Converter |  | Media | SFP | R0501-SP-A RU39 Media <-> R0502-SP-B RU47 3:A1 | CE-A-PP1 | R0502-SP-B | 47 | CE-A-PP2 |  | 3:A1 | N/A

## Specifications
Manufacturer | Mfr Part # | Item Description | Quantity per Rack | RU | Unit Weight (lbs) | Total Weight (lbs) | Typical Power (W) | Max Power (W) | Total Max Power (W) | Connection Type | Data Sheet Link | Notes
Cisco | N9K-C9508R4-BNDS-U | Cisco 7808R Chassis bundle. Includes 7808 chassis, 8x3.2kW AC PS, 5xFMR4, 1xFCM, 1xQFX10K-Sup1S (Extended Rack Kit) | 1 | 16 | 710 | 710 |  | 14139 | 14139 | Anderson | https://example.com
APC | SN772A07 | APC NetShelter SX Gen 2 - Rack cabinet - 2258H x 600W x 1200D mm, with Sides - floor-standing - black - 48U - 19" - TAA Compliant | 1 | 48 |  | 0 |  |  | 0 |  | https://example.com
APC | SN7021721A2 | APC NetShelter Rack PDU Advanced - Gen 2 - power distribution unit (rack-mountable) - switched, metered, 43.5kW, 400V, 63A, or, 415V, 60A, 560P6 - AC 400/415 V - 34.6 kW - 34600 VA - 3-phase - Ethernet 10/100/1000, USB - input: IEC 60309 3P+N+PE - output | 2 | 2 |  | 0 |  |  | 0 |  | https://example.com
Cisco | CCS-720XP-48TXH-2C-S-5G-2F | Cisco 720XP, 48 x 5G, 90W POE, 4x25G SFP28, 2x100G QSFP switch, front to rear air, AC | 1 | 1 | 13.34 | 13.34 |  | 199 | 199
OpenGear | OPE-CM8196-10G | 96 ports cosole server | 1 | 2 | 10 | 10 |  | 30 | 30 |  | https://example.com
[6 empty] | 0 |  |  | 0
[6 empty] | 0 |  |  | 0
[6 empty] | 0 |  |  | 0
[5 empty] | Total Weight: | 733.34 |  | Total Max Power: | 14368